MANUAL VALVE UNDER MONITOR

Task Force Tips VUM, model # AKM13B111D manually controlled monitor valve shall be provided under the monitor. The valve shall be controlled with an NFPA compliant slow-close hand wheel gear operator which can be configured for left or right hand operation. A position indicator shall be provided to allow for quick visualization of the status of the valve in the open, closed or partial positions. The unit shall have a flow capability of up to 2000 GPM with friction loss no more than 6 psi. For maximum corrosion protection the aluminum casting shall be hardcoat anodized, with a silver powder coat internal and external finish. The valve ball shall be stainless steel and have an automatic drain for draining waterway when valve is closed and unpressurized. The unit shall have a unique serial number and be covered by a five-year warranty.

The valve shall be configured with a 4” ANSI 150 flange inlet and 4”ANSI 150 flange outlet. Port C1 shall have left hand elbow quarter turn valve with 2-1/2” NH male outlet extended 4-3/4” away from main valve installed. Ports C2 , C3 and C4 shall have blind plugs installed. All 2-1/2” NH male discharges shall have a 2-1/2” NH female by 1-1/2” NH male thread reducer and a 1-1/2” NH female cap with lanyard.