MANUAL VALVE UNDER MONITOR

Task Force Tips VUM, model # AKP12111CD manually controlled monitor valve shall be provided under the monitor. The valve shall be controlled with an NFPA compliant slow-close crank handle gear operator. A position indicator shall be provided to allow for quick visualization of the status of the valve in the open, closed or partial positions. The unit shall have a flow capability of up to 2000 GPM with friction loss no more than 6 psi. For maximum corrosion protection the aluminum casting shall be hardcoat anodized, with a silver powder coat internal and external finish. The valve ball shall be stainless steel and have an automatic drain for draining waterway when valve is closed and unpressurized. The unit shall have a unique serial number and be covered by a five-year warranty.

The valve shall be configured with a 4" ANSI 150 flange inlet and TFT Code RPM male connection angled at 22.5° for a Task Force Tips monitor with TFT Code RPF female inlet. Ports C1, C2 and C3 shall have blind plugs installed. Port C4 shall have a right hand elbow quarter turn valve with 2-1/2” NH male outlet, extended 4-3/4” from main valve, installed. All 2-1/2” NH male discharges shall have a 2-1/2” NH female by 1-1/2” NH male thread reducer and a 1-1/2” NH female cap with lanyard.