
MASTER STREAM NOZZLE
Task Force Tips model # M-RS1000-NN selectable flow master stream nozzle shall be provided. The nozzle shall be designed for use on monitors, ladder pipes, deluge guns and aerial platforms. For corrosion resistance the nozzle shall be constructed for lightweight hardcoat anodized aluminum.
The nozzle shall have a selectable flow rating of 250 to 1000 GPM at a pressure of 100 PSI. The flow rating shall be user adjustable by depressing the outer baffle and selecting the desired flow. The various ratings shall be laser engraved on the baffle.
The following GPM flows are available
250
350
500
750
1000
A UV resistant rubber bumper with integral teeth designed to produce a finger free fog pattern shall be included. A halo ring shall be included to assist with stream shape control. The nozzle shall be suitable for foam solution application and designed to accept the Task Force Tips FJ-LX-M low expansion air aspirating attachment. The nozzle shall be configured with a 3-1/2" female NH swivel rocker lug coupling.

