
2000 GPM FIXED LOCATION MONITOR
Task Force Tips Monsoon model # Y4-T61A manually controlled monitor shall be provided. The monitor shall operate with a hand wheel which controls a stainless steel worm gear for elevation adjustment and a long tiller bar for rotation adjustment and include a locking knob.
The monitor shall have the following capabilities: 
Full horizontal rotation with continuous 360 degree travel;
135 degrees of vertical travel from 45 degrees below and 90 degrees above horizontal;
Field changeable elevation stops at 30 and 45 degrees above horizontal and 30 degrees below horizontal;
Field changeable rotation stops shall be provided at 45, 90 and 135 degrees left and/or right of center;
Flow capability of 2000 GPM with a friction loss of no more than 16 psi;
Maximum operating pressure of 200 PSI.
For resistance to corrosion the monitor shall be constructed from hardcoat anodized aluminum with a silver powder coat interior and exterior finish. A threaded port for an optional pressure gauge shall be provided. The unit shall have a unique serial number and be covered by a five-year warranty.
The monitor shall be designed with a unique waterway that minimizes the path of travel, reduces friction loss and turbulence, and produces a far reaching water stream. The monitor shall be configured with a 3" female NPT inlet and 3-1/2" male NH outlet. The unit shall be covered by a five-year warranty.

