
1500 GPM FIXED LOCATION  MONITOR
Task Force Tips Typhoon, model # Y5-DS1A manually controlled monitor shall be provided. The Monitor shall operate with a hand wheel for rotation adjustment, and a hand wheel for elevation adjustment. 
The monitor shall have the following capabilities: 
Full horizontal rotation with 360 degree travel; 
135 degrees of vertical travel from 90 degrees above horizontal to 45 degrees below horizontal
Field changeable rotation hard stops shall be provided at 45, 90 and/or 135 degrees left and right of center;
Field changeable hard stops in 10 degree increments left and/or right, and above and/or below horizontal;
Flow capability of 1500 GPM with 19 PSI of friction loss;
Maximum operating pressure of 200 PSI
For resistance to corrosion the monitor shall be constructed from hardcoat anodized aluminum with a silver powder coat interior and exterior finish. The discharge elbow shall include an integral stream straightener. A threaded port for an optional pressure gauge shall be provided. The unit shall have a unique serial number and be covered by a five-year warranty.
The monitor shall be configured with a 4-1/2" female NH quick disconnect coupling with locking pin  on a 4" female NPT inlet and 3-1/2" male NH outlet. 

