## Sheet1
Side Load Mounting Points for Task Force Tips Extend-A-Gun, 12" Models.
WARNING: Before installing the Extend-A-Gun you MUST determine the forces that will be exerted in the proposed installation by the reaction forces of the nozzle.
Refer to Model XG12 Extend-A-Gun Installation and Operating Instructions, TFT Literature # LIX-512.
1. Determine the distance, D1, in inches, from the center of the monitor elevation joint to the bottom of the threads in the monitor inlet. Enter this in green box D1.
D1 FOR MOST COMMON INSTALLATIONS
Task Force Tips CROSSFIRE D1 = 1"
Elkhart Stinger Model 8297-98 w/companion flange D1 = 6"
Akron Apollo Model 3422 w/companion flange D1 = 5"
Akron Apollo Model 3422 threaded on D1 = 4"
CHARTS FOR MODEL XG12 ONLY
D1 = | inches
[5 empty] | D1 | D2 | HEIGHT | D3 min | D3 max | D1 | D2 | HEIGHT | D3 min | D3 max
2. Locate the value of D1, in the charts on right. Find the desired HEIGHT from the center of the upper bracket to the center of the stream in the HEIGHT column. |  |  |  |  | 1 | 1 | 18 | 7 | 14 | 6 | 1 | 23 | 9 | 14
[6 empty] | 2 | 19 | 8 | 13 |  | 2 | 24 | 10 | 13
[6 empty] | 3 | 20 | 8 | 12 |  | 3 | 25 | 10 | 12
[6 empty] | 4 | 21 | 8 | 11 |  | 4 | 26 | 11 | 11
3. Locate D2, the distance from the bottom of the latch casting to the center of the upper mounting bracket, for the chosen HEIGHT. (inches). Enter this in green box D2. | [5 empty] | 5 | 22 | 9 | 10
[6 empty] | 6 | 23 | 9 | 9
D2 = | inches
4. Determine the distance, D3 in inches, from the center of the upper mounting bracket to the center of the lower mounting bracket for the proposed installation. D3 MUST be between D3 min and D3 max. Enter this in green box D3. |  |  |  |  | D1 | D2 | HEIGHT | D3 min | D3 max | D1 | D2 | HEIGHT | D3 min | D3 max
[5 empty] | 2 | 1 | 19 | 8 | 14 | 7 | 1 | 24 | 10 | 14
[6 empty] | 2 | 20 | 8 | 13 |  | 2 | 25 | 10 | 13
[6 empty] | 3 | 21 | 8 | 12 |  | 3 | 26 | 11 | 12
D3= | inches |  |  |  |  | 4 | 22 | 9 | 11 |  | 4 | 27 | 11 | 11
[6 empty] | 5 | 23 | 9 | 10
5. Calculate forces on Brackets, Add D1 + D2 + D3 + 15.7 = L (inches) |  |  | L= | 15.7
6. Multiply L x 900 = M (inch/pounds) |  |  | M= | 14130
7. Divide M by D3 = F1 (pounds) |  | MUST be < 3100 lbf. | F1= | #DIV/0! | D1 | D2 | HEIGHT | D3 min | D3 max | D1 | D2 | HEIGHT | D3 min | D3 max
[5 empty] | 3 | 1 | 20 | 8 | 14 | 8 | 1 | 25 | 10 | 14
8. Subtract 900 from F1 = F2 (pounds) |  | MUST be < 2200 lbf. | F2= | #DIV/0! |  | 2 | 21 | 8 | 13 |  | 2 | 26 | 11 | 13
[6 empty] | 3 | 22 | 9 | 12 |  | 3 | 27 | 11 | 12
NOTE: F1 MUST be less than 3100 lbf. F2 MUST be less than 2200 lbf. and the proposed installation MUST be capable of withstanding forces of this magnitude. | [5 empty] | 4 | 23 | 9 | 11 |  | 4 | 28 | 11 | 11
[6 empty] | 5 | 24 | 10 | 10
WARNING: Injury can result from an inadequately supported monitor. The monitor mount must be capable of supporting the nozzle reaction force which can be as high as 900 lbf. (400 kg). Flanges and pipe made from plastic are inadequate for monitor mounting and must not be used.
[5 empty] | D1 | D2 | HEIGHT | D3 min | D3 max | D1 | D2 | HEIGHT | D3 min | D3 max
[5 empty] | 4 | 1 | 21 | 8 | 14 | 9 | 1 | 26 | 11 | 14
[6 empty] | 2 | 22 | 9 | 13 |  | 2 | 27 | 11 | 13
[6 empty] | 3 | 23 | 9 | 12 |  | 3 | 28 | 11 | 12
[6 empty] | 4 | 24 | 10 | 11
[6 empty] | 5 | 25 | 10 | 10
[5 empty] | D1 | D2 | HEIGHT | D3 min | D3 max | D1 | D2 | HEIGHT | D3 min | D3 max
[5 empty] | 5 | 1 | 2 | 9 | 14 | 10 | 1 | 27 | 11 | 14
[6 empty] | 2 | 23 | 9 | 13 |  | 2 | 28 | 11 | 13
[6 empty] | 3 | 24 | 10 | 12 |  | 3 | 29 | 12 | 12
[6 empty] | 4 | 25 | 10 | 11